# Valve actuator: SAUTER vialoq AVM 1000

Make:   AVM322SF132

## Area of application

In ventilation and air conditioning systems for actuating 2-way and 3-way valves of the V6R, VQD, VQE, VUG, VUP, VUS, B6R, BQD, BQE, BUG, BUS series. For controllers with constant output (0...10 V or 4...20 mA) or switching output (2-point or 3-point control).

## Performance features

- Valve actuator with patented toolless actuator/valve coupling (quick-release).

- Low energy consumption.

- Crank handle for external manual adjustment with motor cut-off.

- Operating indicator with two-colour LED (operation, initialisation, actuation, end positions and overload).

- Electrical connection using plug-in screw terminals up to 1.5 mm².

- With low-noise gear unit and electric, power-dependent motor cut-off.

- Integrated forced operation with selectable direction of action using coding switch.

## Technical data

General information

| Power supply: | 24 V~/= |
| --- | --- |
| Actuating power: | 1000 N |
| Stroke: | 20 mm |
| Selectable positioning time: | 6 or 12 s/mm |
| Inputs: | 0… 10 V= 4...20 mA 2-point or 3-point |
| Positioner direction of action: | Selectable |
| Positional feedback signal: | 0…10 V= |
| Selectable valve characteristic: | Linear / equal percentage |
| Operating noise: | < 30 dB(A) |
| Connection module: | Pluggable screw terminal for conductor cross-section of max. 1.5 mm2 |
| Dimensions, W x H x D: | 160 x 187 x 88 mm |

Power consumption

| During operation: | < 1.7 W < 3.5 VA |
| --- | --- |
| At standstill: | < 0.45 W |

Admissible ambient conditions

| Operating temperature: | -10…55 °C |
| --- | --- |
| Storage and transport temperature: | -40…80 °C |
| Humidity: | 5…85% rh |
| Ingress protection: | IP 54 |

Accessories

| 0372336180 | Temperature adaptor for media temperature > 100 °C … 150 °C |
| --- | --- |
| 0372336240 | Temperature adaptor for media temperature > 130°C … 200°C |
| 0510220001 | Configuration tool for Case Drives |
| 0500420001 | Split-range unit module |
| 0500420002 | 4...20 mA feedback module |
| 0500420003 | Constant 230V module |
| 0510600001 | Cable module, 1.2 m, 3-wire, PVC |
| 0510600002 | Cable module, 1.2 m, 3-wire, halogen-free |
| 0510600003 | Cable module, 1.2 m, 6-wire, PVC |
| 0510600004 | Cable module, 1.2 m, 6-wire, halogen-free |
| 0510600005 | Cable module, 5 m, 3-wire, PVC |
| 0510600006 | Cable module, 5 m, 3-wire, halogen-free |
| 0510600007 | Cable module, 5 m, 6-wire, PVC |
| 0510600008 | Cable module, 5 m, 6-wire, halogen-free |
| 0510240012 | Mounting set V6.. / B6... up to 20 mm stroke |
| 0510390006 | Adaptations for non-SAUTER valves by Siemens For stroke up to 20 mm and spindle diameter of 10 mm |
| 0510390013 | Adaptations for non-SAUTER valves by Siemens For stroke up to 20 mm and spindle diameter of 14 mm |
| 0510390007 | Adaptations for non-SAUTER valves by JCI |
| 0510390008 | Adaptations for non-SAUTER valves by Honeywell |
| 0510390009 | Adaptations for non-SAUTER valves by LDM |
| 0510390010 | Adaptations for ITT-Dräger |
| 0510390012 | Adaptations for non-SAUTER valves by Belimo |

Manufacturer: Fr. Sauter AG, Basel